## register
id | parameter | value | unit | type | source_title | source_url | accessed | notes
re_target_2030 | Renewable share of electricity generation, 2030 | 0.35 | share | sourced | TAP, 9 Oct 2026: Head of Government reaffirms 35% target | https://www.tap.info.tn/fr/Portail-%C3%A0-la-Une-FR-top/20672933-%C3%A9nergie-la | 2026-10-27 | Older documents (ANME, AICS) say 30%; raised to 35% in June 2022 (REGlobal).
flex_cap_mw | Shiftable load cap (scenario S2-300) | 300 | MW | sourced | TAP, 9 Oct 2026: action plan targets 300 MW peak-demand reduction | https://www.tap.info.tn/fr/Portail-%C3%A0-la-Une-FR-top/20672933-%C3%A9nergie-la | 2026-10-27 | Official peak-reduction figure used as size of demand shifting.
flex_cap_hi_mw | Shiftable load cap, sensitivity (S2-600) | 600 | MW | assumption |  |  | 2026-10-27 | 2 x official 300 MW figure (spec D5).
flex_max_hours | Maximum shift duration | 3 | h | assumption |  |  | 2026-10-27 | 'A few hours' in the project brief (spec D5).
gas_price_factor_lo | Gas price sensitivity, low | 0.5 | x base | assumption |  |  | 2026-10-27 | -50% (spec D8).
gas_price_factor_hi | Gas price sensitivity, high | 1.5 | x base | assumption |  |  | 2026-10-27 | +50% (spec D8).
demand_growth | Electricity demand growth rate (STEG base case, applied 2024 -> 2030) | 0.032 | 1/yr | sourced | JICA / TEPSCO / KPMG, Data Collection Survey on Power Sector in Tunisia, Final Report (Mar 2022), quoting STEG's base-case forecast, p.2-17 and p.5-34 | https://openjicareport.jica.go.jp/pdf/12342283.pdf | 2026-10-28 | STEG base case (current trend): 'the annual growth rate is 3.2%' compared to 2019 actuals (p.2-17). Author's choice (2026-10-28). Other figures: REGlobal 3.7% (names no source); STEG 2025 actual +4.1% (steg.com.tn/fr/page/produire); government trend 4-5%/yr (pm.gov.tn/en/node/3133, Aug 2026). Applied to the ONEM 2024 total: 22.507 x 1.032^6 = 27.2 TWh in 2030, vs STEG's 28.4 TWh (different base year and demand definition).
peak_ref_2030_mw | Reference 2030 peak demand | 6000 | MW | sourced | JICA / TEPSCO / KPMG, Data Collection Survey on Power Sector in Tunisia, Final Report (Mar 2022), quoting STEG's base-case forecast, p.2-17 and p.5-35 | https://openjicareport.jica.go.jp/pdf/12342283.pdf | 2026-10-28 | STEG forecast: 'maximum power of 6000 MW ... around 15:00 during the daytime in July' 2030 (p.5-35). Measured peaks: 4,888 MW (14 Aug 2024), 4,837 MW (25 Jul 2025). Warning check only (spec §5.1).
discount_rate | Discount rate for annualising investment | 0.071 | 1/yr | sourced | PyPSA-Earth v0.10.0 config.default.yaml, costs.discountrate | https://github.com/pypsa-meets-earth/pypsa-earth/blob/v0.10.0/config.default.yaml | 2026-10-27 | Same rate as the full PyPSA-Earth model, so toy and model are consistent.
demand_2024_twh | Electricity demand 2024 (generation + net imports) | 22.507 | TWh | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025), table 'ELECTRICITE', printed p.18 | https://www.energiemines.gov.tn/fileadmin/docs-u1/Chiffres_cl%C3%A9s_%C3%A9nergie_2024.pdf | 2026-10-28 | Sum of the 2024 column (GWh): STEG 18,617 + IPP solar 34 + self-generation solar 557 + third-party purchases 187 + exchanges -1.1 - exports 107.9 + imports 3,221 = 22,507. Excludes self-consumed thermal self-generation. Cross-check: Ember gives 23.96 TWh (gross generation + net imports), about 6% higher. Author chose ONEM (2026-10-28).
imports_2024_twh | Net electricity imports 2024 | 3.1131 | TWh | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025), table 'ELECTRICITE', printed p.18 | https://www.energiemines.gov.tn/fileadmin/docs-u1/Chiffres_cl%C3%A9s_%C3%A9nergie_2024.pdf | 2026-10-28 | Net imports = imports 3,221 - exports 107.9 GWh (2024). Mainly Algeria and Libya. Cross-check: Ember net imports 2.59 TWh.
gas_price_eur_per_mwh_th | Natural gas price (economic cost) | 28.4158 | EUR/MWh_th | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (gas, fuel); original: World Bank Commodity Markets 2025 and ENTSO-E/ENTSOG TYNDP 2024 | https://github.com/PyPSA/technology-data/blob/v0.15.0/outputs/costs_2030.csv | 2026-10-28 | Economic (import-parity) gas price, as used by PyPSA-Earth v0.10.0; not STEG's subsidised tariff (spec D8).
toy_ccgt_investment | CCGT investment | 1108.7166 | EUR/kW | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (CCGT, investment); original: Danish Energy Agency, inputs/technology_data_for_el_and_dh.xlsx | https://github.com/PyPSA/technology-data/blob/v0.15.0/outputs/costs_2030.csv | 2026-10-27 | Toy model input (Phase 1); same cost file as PyPSA-Earth v0.10.0.
toy_ccgt_fom | CCGT fixed O&M | 3.3494 | %/year | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (CCGT, FOM); original: Danish Energy Agency, inputs/technology_data_for_el_and_dh.xlsx | https://github.com/PyPSA/technology-data/blob/v0.15.0/outputs/costs_2030.csv | 2026-10-27 | Toy model input (Phase 1); same cost file as PyPSA-Earth v0.10.0.
toy_ccgt_vom | CCGT variable O&M | 5.6104 | EUR/MWh | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (CCGT, VOM); original: Danish Energy Agency, inputs/technology_data_for_el_and_dh.xlsx | https://github.com/PyPSA/technology-data/blob/v0.15.0/outputs/costs_2030.csv | 2026-10-27 | Toy model input (Phase 1); same cost file as PyPSA-Earth v0.10.0.
toy_ccgt_efficiency | CCGT electrical efficiency | 0.58 | per unit | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (CCGT, efficiency); original: Danish Energy Agency, inputs/technology_data_for_el_and_dh.xlsx | https://github.com/PyPSA/technology-data/blob/v0.15.0/outputs/costs_2030.csv | 2026-10-27 | Toy model input (Phase 1); same cost file as PyPSA-Earth v0.10.0.
toy_ccgt_lifetime | CCGT lifetime | 25 | years | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (CCGT, lifetime); original: Danish Energy Agency, inputs/technology_data_for_el_and_dh.xlsx | https://github.com/PyPSA/technology-data/blob/v0.15.0/outputs/costs_2030.csv | 2026-10-27 | Toy model input (Phase 1); same cost file as PyPSA-Earth v0.10.0.
toy_solar_investment | Utility PV investment | 482.4785 | EUR/kW_e | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (solar-utility, investment); original: Danish Energy Agency, inputs/technology_data_for_el_and_dh.xlsx | https://github.com/PyPSA/technology-data/blob/v0.15.0/outputs/costs_2030.csv | 2026-10-27 | Toy model input (Phase 1); same cost file as PyPSA-Earth v0.10.0.
toy_solar_fom | Utility PV fixed O&M | 2.4757 | %/year | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (solar-utility, FOM); original: Danish Energy Agency, inputs/technology_data_for_el_and_dh.xlsx | https://github.com/PyPSA/technology-data/blob/v0.15.0/outputs/costs_2030.csv | 2026-10-27 | Toy model input (Phase 1); same cost file as PyPSA-Earth v0.10.0.
toy_solar_lifetime | Utility PV lifetime | 40 | years | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (solar-utility, lifetime); original: Danish Energy Agency, inputs/technology_data_for_el_and_dh.xlsx | https://github.com/PyPSA/technology-data/blob/v0.15.0/outputs/costs_2030.csv | 2026-10-27 | Toy model input (Phase 1); same cost file as PyPSA-Earth v0.10.0.
toy_onwind_investment | Onshore wind investment | 1383.3059 | EUR/kW | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (onwind, investment); original: Danish Energy Agency, inputs/technology_data_for_el_and_dh.xlsx | https://github.com/PyPSA/technology-data/blob/v0.15.0/outputs/costs_2030.csv | 2026-10-27 | Toy model input (Phase 1); same cost file as PyPSA-Earth v0.10.0.
toy_onwind_fom | Onshore wind fixed O&M | 1.2167 | %/year | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (onwind, FOM); original: Danish Energy Agency, inputs/technology_data_for_el_and_dh.xlsx | https://github.com/PyPSA/technology-data/blob/v0.15.0/outputs/costs_2030.csv | 2026-10-27 | Toy model input (Phase 1); same cost file as PyPSA-Earth v0.10.0.
toy_onwind_vom | Onshore wind variable O&M | 1.8033 | EUR/MWh | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (onwind, VOM); original: Danish Energy Agency, inputs/technology_data_for_el_and_dh.xlsx | https://github.com/PyPSA/technology-data/blob/v0.15.0/outputs/costs_2030.csv | 2026-10-27 | Toy model input (Phase 1); same cost file as PyPSA-Earth v0.10.0.
toy_onwind_lifetime | Onshore wind lifetime | 30 | years | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (onwind, lifetime); original: Danish Energy Agency, inputs/technology_data_for_el_and_dh.xlsx | https://github.com/PyPSA/technology-data/blob/v0.15.0/outputs/costs_2030.csv | 2026-10-27 | Toy model input (Phase 1); same cost file as PyPSA-Earth v0.10.0.
toy_battery_storage_investment | Battery energy (storage) investment | 189.861 | EUR/kWh | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (battery storage, investment); original: Danish Energy Agency, inputs/technology_data_catalogue_for_energy_storage.xlsx | https://github.com/PyPSA/technology-data/blob/v0.15.0/outputs/costs_2030.csv | 2026-10-27 | Toy model input (Phase 1); same cost file as PyPSA-Earth v0.10.0.
toy_battery_storage_lifetime | Battery energy (storage) lifetime | 25 | years | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (battery storage, lifetime); original: Danish Energy Agency, inputs/technology_data_catalogue_for_energy_storage.xlsx | https://github.com/PyPSA/technology-data/blob/v0.15.0/outputs/costs_2030.csv | 2026-10-27 | Toy model input (Phase 1); same cost file as PyPSA-Earth v0.10.0.
toy_battery_inverter_investment | Battery inverter (power) investment | 213.9279 | EUR/kW | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (battery inverter, investment); original: Danish Energy Agency, inputs/technology_data_catalogue_for_energy_storage.xlsx | https://github.com/PyPSA/technology-data/blob/v0.15.0/outputs/costs_2030.csv | 2026-10-27 | Toy model input (Phase 1); same cost file as PyPSA-Earth v0.10.0.
toy_battery_inverter_fom | Battery inverter fixed O&M | 0.3375 | %/year | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (battery inverter, FOM); original: Danish Energy Agency, inputs/technology_data_catalogue_for_energy_storage.xlsx | https://github.com/PyPSA/technology-data/blob/v0.15.0/outputs/costs_2030.csv | 2026-10-27 | Toy model input (Phase 1); same cost file as PyPSA-Earth v0.10.0.
toy_battery_inverter_efficiency | Battery round-trip efficiency (source: 'Round trip efficiency DC') | 0.96 | per unit | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (battery inverter, efficiency); original: Danish Energy Agency, inputs/technology_data_catalogue_for_energy_storage.xlsx | https://github.com/PyPSA/technology-data/blob/v0.15.0/outputs/costs_2030.csv | 2026-10-27 | Toy model input (Phase 1); round trip, so each direction uses its square root (as PyPSA-Earth). Source pinned by the v0.15.0 tag.
toy_battery_inverter_lifetime | Battery inverter lifetime | 10 | years | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (battery inverter, lifetime); original: Danish Energy Agency, inputs/technology_data_catalogue_for_energy_storage.xlsx, Note K. | https://github.com/PyPSA/technology-data/blob/v0.15.0/outputs/costs_2030.csv | 2026-10-27 | Toy model input (Phase 1); same cost file as PyPSA-Earth v0.10.0.
toy_gas_fuel | Natural gas fuel cost | 28.4158 | EUR/MWh_th | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (gas, fuel); original: World Bank (2025) Commodity Markets, https://www.worldbank.org/en/research/commodity-markets; and ENTSO-E & ENTSOG TYNDP 2024 Scenarios Inputs Commodity Prices, https://2024-data.entsos-tyndp-scenarios.eu/files/scenarios-inputs/Prices.zip, accessed: 2026-02-03. | https://github.com/PyPSA/technology-data/blob/v0.15.0/outputs/costs_2030.csv | 2026-10-27 | Toy model input (Phase 1); same cost file as PyPSA-Earth v0.10.0.
toy_gas_co2_intensity | Natural gas CO2 intensity | 0.198 | tCO2/MWh_th | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (gas, CO2 intensity); original: Stoichiometric calculation with 50 GJ/t CH4 | https://github.com/PyPSA/technology-data/blob/v0.15.0/outputs/costs_2030.csv | 2026-10-27 | Toy model input (Phase 1); same cost file as PyPSA-Earth v0.10.0.
toy_battery_max_hours | Toy battery energy-to-power ratio | 4 | h | assumption |  |  | 2026-10-27 | Toy only: fixed storage duration so the battery is one StorageUnit; the full model sizes energy separately.
cap_2024_ccgt_mw | Net installed capacity 2024: combined cycle | 2527 | MW | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) | https://www.energiemines.gov.tn/fileadmin/docs-u1/Chiffres_cl%C3%A9s_%C3%A9nergie_2024.pdf | 2026-10-28 | Read from the chart 'Parc de production électrique net 2023-2024', printed p.17 (no text layer). Check: text on the same page says combined cycles are 42% of the fleet; 2527/6012 = 42.0%.
cap_2024_ocgt_mw | Net installed capacity 2024: gas turbines (open cycle) | 2457 | MW | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) | https://www.energiemines.gov.tn/fileadmin/docs-u1/Chiffres_cl%C3%A9s_%C3%A9nergie_2024.pdf | 2026-10-28 | Read from the chart 'Parc de production électrique net 2023-2024', printed p.17 (no text layer). Check: text on the same page says combined cycles are 42% of the fleet; 2527/6012 = 42.0%.
cap_2024_steam_mw | Net installed capacity 2024: steam turbines | 660 | MW | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) | https://www.energiemines.gov.tn/fileadmin/docs-u1/Chiffres_cl%C3%A9s_%C3%A9nergie_2024.pdf | 2026-10-28 | Read from the chart 'Parc de production électrique net 2023-2024', printed p.17 (no text layer). Check: text on the same page says combined cycles are 42% of the fleet; 2527/6012 = 42.0%. Note: JICA 2022 p.5-36 says STEG planned to retire 660 MW of thermal capacity before 2026 and 360 MW more by 2030 (thermal fleet 6,491 MW in 2030 incl. new units). Check the 2030 fleet in Task 10 (spec D6).
cap_2024_re_mw | Net installed capacity 2024: renewables (hydro + wind + solar, centralised) | 368 | MW | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) | https://www.energiemines.gov.tn/fileadmin/docs-u1/Chiffres_cl%C3%A9s_%C3%A9nergie_2024.pdf | 2026-10-28 | Read from the chart 'Parc de production électrique net 2023-2024', printed p.17 (no text layer). Check: text on the same page says combined cycles are 42% of the fleet; 2527/6012 = 42.0%.
cap_2024_total_mw | Net installed capacity 2024: total | 6012 | MW | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) | https://www.energiemines.gov.tn/fileadmin/docs-u1/Chiffres_cl%C3%A9s_%C3%A9nergie_2024.pdf | 2026-10-28 | Read from the chart 'Parc de production électrique net 2023-2024', printed p.17 (no text layer). Check: text on the same page says combined cycles are 42% of the fleet; 2527/6012 = 42.0%.
gen_2024_gas_twh | Electricity generation 2024: natural gas | 18.156 | TWh | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) | https://www.energiemines.gov.tn/fileadmin/docs-u1/Chiffres_cl%C3%A9s_%C3%A9nergie_2024.pdf | 2026-10-28 | Table 'PRODUCTION D'ELECTRICITE', printed p.18, row GAZ NATUREL. Excludes thermal self-generators.
gen_2024_oil_twh | Electricity generation 2024: fuel oil + gasoil | 0.0719 | TWh | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) | https://www.energiemines.gov.tn/fileadmin/docs-u1/Chiffres_cl%C3%A9s_%C3%A9nergie_2024.pdf | 2026-10-28 | Same table, row FUEL + GASOIL (71.9 GWh).
gen_2024_hydro_twh | Electricity generation 2024: hydro | 0.016 | TWh | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) | https://www.energiemines.gov.tn/fileadmin/docs-u1/Chiffres_cl%C3%A9s_%C3%A9nergie_2024.pdf | 2026-10-28 | Same table, row HYDRAULIQUE (16 GWh).
gen_2024_wind_twh | Electricity generation 2024: wind | 0.337 | TWh | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) | https://www.energiemines.gov.tn/fileadmin/docs-u1/Chiffres_cl%C3%A9s_%C3%A9nergie_2024.pdf | 2026-10-28 | Same table, row EOLIENNE (337 GWh).
gen_2024_solar_twh | Electricity generation 2024: solar PV (STEG + IPP + self-generation) | 0.6278 | TWh | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) | https://www.energiemines.gov.tn/fileadmin/docs-u1/Chiffres_cl%C3%A9s_%C3%A9nergie_2024.pdf | 2026-10-28 | Same table: STEG solar 36.8 + 'IPP + autoproducteurs (Solaire)' 591 GWh.
gen_2024_total_twh | Electricity generation 2024: total | 19.208 | TWh | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) | https://www.energiemines.gov.tn/fileadmin/docs-u1/Chiffres_cl%C3%A9s_%C3%A9nergie_2024.pdf | 2026-10-28 | Same table, row TOTAL (19,208 GWh).
gas_share_2024 | Gas share of electricity generation 2024 | 0.945 | share | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) | https://www.energiemines.gov.tn/fileadmin/docs-u1/Chiffres_cl%C3%A9s_%C3%A9nergie_2024.pdf | 2026-10-28 | Pie 'Mix de la production électricité pour l'année 2024', printed p.18 (94.5%, including PV self-generation). Denominator = generation. Ember gives 94.52% of generation; ~85% figures elsewhere divide by demand incl. imports (risk R7).
peak_2024_mw | Peak electricity demand 2024 | 4888 | MW | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) | https://www.energiemines.gov.tn/fileadmin/docs-u1/Chiffres_cl%C3%A9s_%C3%A9nergie_2024.pdf | 2026-10-28 | Printed p.19: record peak of 4888 MW on 14 Aug 2024.
steg_specific_consumption_2024 | STEG fleet specific fuel consumption 2024 | 194.8 | toe(GCV)/GWh | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) | https://www.energiemines.gov.tn/fileadmin/docs-u1/Chiffres_cl%C3%A9s_%C3%A9nergie_2024.pdf | 2026-10-28 | Table 'Consommation spécifique des moyens de production', printed p.19. Gross calorific value basis. For calibrating fleet efficiency in Task 10.
steg_demand_2030_gwh | STEG forecast of 2030 electricity demand | 28362 | GWh | sourced | JICA / TEPSCO / KPMG, Data Collection Survey on Power Sector in Tunisia, Final Report (Mar 2022), quoting STEG's base-case forecast, p.2-17 | https://openjicareport.jica.go.jp/pdf/12342283.pdf | 2026-10-28 | STEG base-case 2030 demand. For comparison only; our 2030 demand is the ONEM 2024 total grown at demand_growth (spec D2).
load_factor_2030 | STEG 2030 forecast: annual load factor | 0.54 | share | sourced | JICA / TEPSCO / KPMG, Data Collection Survey on Power Sector in Tunisia, Final Report (Mar 2022), quoting STEG's base-case forecast, p.5-34 | https://openjicareport.jica.go.jp/pdf/12342283.pdf | 2026-10-28 | 'the load factor is 54%' for STEG's 2030 forecast. Used to check the hourly demand shape (risk R5).
min_to_peak_2030 | STEG 2030 forecast: minimum-to-peak load ratio | 0.34 | share | sourced | JICA / TEPSCO / KPMG, Data Collection Survey on Power Sector in Tunisia, Final Report (Mar 2022), quoting STEG's base-case forecast, p.5-35 | https://openjicareport.jica.go.jp/pdf/12342283.pdf | 2026-10-28 | 2030 minimum 2,064 MW (around 7:00 in February) / maximum 6,000 MW = 34% (stated). Shape check (risk R5).
ccgt_efficiency | CCGT electrical efficiency (new build) | 0.58 | per unit | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (CCGT, efficiency); original: Danish Energy Agency, inputs/technology_data_for_el_and_dh.xlsx | https://github.com/PyPSA/technology-data/blob/v0.15.0/outputs/costs_2030.csv | 2026-10-28 | Same cost file as PyPSA-Earth v0.10.0. Efficiencies are on net calorific value (LHV).
ccgt_vom | CCGT variable O&M | 5.6104 | EUR/MWh | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (CCGT, VOM); original: Danish Energy Agency, inputs/technology_data_for_el_and_dh.xlsx | https://github.com/PyPSA/technology-data/blob/v0.15.0/outputs/costs_2030.csv | 2026-10-28 | Same cost file as PyPSA-Earth v0.10.0. Efficiencies are on net calorific value (LHV).
ocgt_efficiency | OCGT electrical efficiency (new build) | 0.41 | per unit | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (OCGT, efficiency); original: Danish Energy Agency, inputs/technology_data_for_el_and_dh.xlsx | https://github.com/PyPSA/technology-data/blob/v0.15.0/outputs/costs_2030.csv | 2026-10-28 | Same cost file as PyPSA-Earth v0.10.0. Efficiencies are on net calorific value (LHV).
ocgt_vom | OCGT variable O&M | 6.0111 | EUR/MWh | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (OCGT, VOM); original: Danish Energy Agency, inputs/technology_data_for_el_and_dh.xlsx | https://github.com/PyPSA/technology-data/blob/v0.15.0/outputs/costs_2030.csv | 2026-10-28 | Same cost file as PyPSA-Earth v0.10.0. Efficiencies are on net calorific value (LHV).
gas_ncv_per_gcv | Natural gas: net / gross calorific value | 0.9 | ratio | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024, conversion table (PDF p.22) | https://www.energiemines.gov.tn/fileadmin/docs-u1/Chiffres_cl%C3%A9s_%C3%A9nergie_2024.pdf | 2026-10-28 | '1PCI = 0,9 PCS'. Converts STEG's specific consumption (gross, PCS) to the net basis of technology-data efficiencies.
existing_gas_efficiency_factor | Efficiency factor for existing gas units (calibrated) | 0.8634 | x tech-data | assumption | Calibrated (Task 10) so the dispatch-only 2024 run matches STEG's measured fuel use: ONEM Memento 2024, specific consumption 194.8 toe(PCS)/GWh, PCI = 0.9 PCS | https://www.energiemines.gov.tn/fileadmin/docs-u1/Chiffres_cl%C3%A9s_%C3%A9nergie_2024.pdf | 2026-10-28 | Calibration, not a published figure. Fitted by scripts/validate_baseline.py so the 2024 dispatch-only run matches STEG's measured fuel use (ONEM Memento 2024: 194.8 toe(PCS)/GWh; PCI = 0.9 PCS). Target 0.490 (net) / model 0.568 at factor 1. Existing CCGT 0.58 x 0.8634 = 0.501; existing OCGT + steam 0.41 x 0.8634 = 0.354. Also absorbs unmodelled outages and part-load operation (the model has no availability limits). New builds keep tech-data values.
ocgt_investment | OCGT investment (new build) | 581.3949 | EUR/kW | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (OCGT, investment); original: Danish Energy Agency, inputs/technology_data_for_el_and_dh.xlsx | https://github.com/PyPSA/technology-data/blob/v0.15.0/outputs/costs_2030.csv | 2026-10-28 | Same cost file as PyPSA-Earth v0.10.0. For the new-build OCGT option (spec D1) and CO2 reporting (D9).
ocgt_fom | OCGT fixed O&M | 1.7795 | %/year | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (OCGT, FOM); original: Danish Energy Agency, inputs/technology_data_for_el_and_dh.xlsx | https://github.com/PyPSA/technology-data/blob/v0.15.0/outputs/costs_2030.csv | 2026-10-28 | Same cost file as PyPSA-Earth v0.10.0. For the new-build OCGT option (spec D1) and CO2 reporting (D9).
ocgt_lifetime | OCGT lifetime | 25 | years | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (OCGT, lifetime); original: Danish Energy Agency, inputs/technology_data_for_el_and_dh.xlsx | https://github.com/PyPSA/technology-data/blob/v0.15.0/outputs/costs_2030.csv | 2026-10-28 | Same cost file as PyPSA-Earth v0.10.0. For the new-build OCGT option (spec D1) and CO2 reporting (D9).
gas_co2_intensity | Natural gas CO2 intensity | 0.198 | tCO2/MWh_th | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (gas, CO2 intensity); original: Stoichiometric calculation with 50 GJ/t CH4 | https://github.com/PyPSA/technology-data/blob/v0.15.0/outputs/costs_2030.csv | 2026-10-28 | Same cost file as PyPSA-Earth v0.10.0. For the new-build OCGT option (spec D1) and CO2 reporting (D9).
gas_for_power_2024_ktep_ncv | Natural gas burnt for electricity 2024 | 3168 | ktep (net CV) | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) | https://www.energiemines.gov.tn/fileadmin/docs-u1/Chiffres_cl%C3%A9s_%C3%A9nergie_2024.pdf | 2026-10-28 | Table of gas demand by use, 'Production d'électricité' 2024 = 3168 ktep-pci (PDF p.13). Cross-check of the fleet efficiency: 18,156 GWh / (3,168 x 11.63) GWh_th = 49.3%, vs 49.0% from specific consumption.
cap_2024_selfgen_solar_lv_mw | Self-generation solar, low voltage (rooftop), cumulative to 2024 | 315 | MW | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) | https://www.energiemines.gov.tn/fileadmin/docs-u1/Chiffres_cl%C3%A9s_%C3%A9nergie_2024.pdf | 2026-10-28 | 'Basse tension 315 MW' (PDF p.19). Not in the centralised fleet total of 6,012 MW.
cap_2024_selfgen_solar_mvhv_mw | Self-generation solar, medium/high voltage, authorised to 2024 | 125 | MW | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) | https://www.energiemines.gov.tn/fileadmin/docs-u1/Chiffres_cl%C3%A9s_%C3%A9nergie_2024.pdf | 2026-10-28 | '323 autorisations octroyées pour une puissance totale de 125 MW' (PDF p.19). Authorisations granted, not confirmed installations.

## README
Assumptions register: every input number of the study, with its source.
How to use
- Code reads sheet 'register' via tn2030.register.load_register(); edit values only in column C (blue).
- type = sourced: needs a source_url. type = assumption: a stated modelling choice. type = pending: yellow, not yet sourced, code cannot use it.
- One row per number; ids are unique and used by the code.
- accessed = date the source was read (YYYY-MM-DD).
Example row: re_target_2030 ¦ Renewable share of electricity generation, 2030 ¦ 0.35 ¦ share ¦ sourced ¦ TAP, 9 Oct 2026 ¦ <url> ¦ 2026-10-27 ¦ note