# The value of energy efficiency in Tunisia's power system (2030)

Rayen Romdhani, Energy Engineering, ENIM (Monastir, Tunisia). October 2026.

Model: PyPSA-Earth v0.10.0 with the study code in this repository. All result numbers come from results/summary.csv and results/avoided.csv; all inputs come from data/assumptions_register.xlsx.

# Summary

Tunisia plans 35% renewable electricity by 2030 and generates almost all the rest from gas (94.5% of generation in 2024). This study asks what each MWh of electricity saved, or moved in time, is worth to the 2030 power system.

| Saving 15% in every hour (S1-15 vs S0) avoids, per MWh saved | Value |
| --- | --- |
| System cost | 60 EUR |
| Gas burnt for power | 0.91 MWh (thermal) |
| CO2 | 0.18 t |
| New capacity | 449 MW per TWh saved per year |

With STEG's 10% reserve margin, the base case needs 423 MW of new gas turbines. A 10% saving already avoids all of them.

Saving first on summer air conditioning (S1-15C) avoids 20% more gas per MWh than an even cut, although only 39% of the saving fits on the cooling load.

Letting 300 MW of load move by up to 3 hours, on top of the 15% saving, cuts another 22 M EUR per year and 0.24 Mt of CO2.

At the base gas price the least-cost system reaches 56% renewables, so the 35% target does not bind. It binds only when gas costs half as much.

# 1. Question and scope

The study measures what one MWh of electricity saved through efficiency, or moved in time through demand flexibility, avoids in 2030: new capacity, gas burnt, system cost and CO2. The renewable target stays in force in every scenario, so the comparison is between systems that all meet it.

The model covers Tunisia only, with two network nodes (north and south), 8,760 hourly steps and the 2013 weather year, solved with the open-source solver HiGHS. It does not include the cost of the efficiency programmes themselves, the planned ELMED link to Italy, or other countries.

# 2. Method

## 2.1 Base network and 2024 calibration

PyPSA-Earth, used unmodified, builds the Tunisian grid, power plants, renewable potentials and hourly demand from open data. Its plant list does not match the official fleet, so the thermal fleet is rebuilt from the ONEM 2024 statistics: 2,527 MW of combined cycle and 3,117 MW of gas turbines and steam units. One efficiency factor for existing gas units is fitted so that a 2024 run burns as much gas as STEG reported. The hourly demand shape is stretched to the official load factor and minimum-to-peak ratio.

| 2024 check (calibrated model) | Model | Official | Difference |
| --- | --- | --- | --- |
| Gas burnt for power (TWh thermal) | 37.0 | 36.8 | +0.4% |
| Gas fleet efficiency (net) | 0.49 | 0.49 | +0.0% |
| Peak demand (MW) | 4,901 | 4,888 | +0.3% |
| Gas share of generation | 93.6% | 94.5% | -1.0% |

The gas-burnt check is independent of the fit: the factor was fitted on STEG's specific consumption, and the gas total comes from a separate ONEM table.

## 2.2 The 2030 system

Demand grows from 22.5 TWh in 2024 at 3.2% per year, STEG's base-case forecast as quoted by JICA (2022). Imports stay at their 2024 level (3.1 TWh, flat over the year), so every MWh saved falls on domestic generation. The model then builds solar, onshore wind, batteries and gas turbines at least cost, using 2030 costs from PyPSA technology-data. In every scenario it must:

produce at least 35% of domestic generation from solar, wind and hydro;

keep firm capacity (gas and hydro) at least 10% above peak demand, STEG's planning margin;

build the committed solar and wind projects (data/committed_projects.csv) and keep the existing fleet.

After each solve the pipeline checks the energy balance, the renewable share, the reserve margin, that no load is shed and that committed and existing capacity is kept. All 11 scenarios pass.

## 2.3 Scenarios

| Scenario | What changes against S0 |
| --- | --- |
| S0 | Base case: 2030 demand, base gas price |
| S1-10, S1-15, S1-20 | Demand 10, 15 or 20% lower in every hour |
| S1-15C | Same 15% of annual energy, taken first from summer cooling load |
| S2-300, S2-600 | S1-15 plus 300 or 600 MW of load that can move by up to 3 hours |
| G-lo-S0, G-lo-S1-15 | S0 and S1-15 with the gas price x0.5 |
| G-hi-S0, G-hi-S1-15 | S0 and S1-15 with the gas price x1.5 |

Shiftable load is modelled as a free, lossless store at each node that starts and ends every day half full. Load can be brought forward or postponed, but every MWh moved must come back within 3 hours, and only one direction is allowed in each hour.

# 3. Results

## 3.1 Main scenarios

|  | S0 | S1-10 | S1-15 | S1-20 | S1-15C | S2-300 | S2-600 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Domestic demand (TWh) | 24.08 | 21.36 | 20.00 | 18.64 | 20.00 | 20.00 | 20.00 |
| New gas turbines (MW) | 423 | 0 | 0 | 0 | 0 | 0 | 0 |
| New solar (MW) | 3,929 | 3,237 | 2,928 | 2,606 | 2,802 | 3,453 | 3,948 |
| New onshore wind (MW) | 2,121 | 1,857 | 1,714 | 1,574 | 1,853 | 1,629 | 1,485 |
| Gas burnt (TWh thermal) | 21.55 | 19.09 | 17.83 | 16.60 | 17.09 | 16.63 | 15.89 |
| CO2 (Mt) | 4.27 | 3.78 | 3.53 | 3.29 | 3.38 | 3.29 | 3.15 |
| Renewable share | 56% | 56% | 56% | 56% | 57% | 58% | 60% |
| System cost (M EUR/yr) | 1,327 | 1,157 | 1,084 | 1,012 | 1,073 | 1,062 | 1,045 |
| Average price (EUR/MWh) | 54.7 | 54.2 | 53.5 | 52.8 | 53.1 | 52.5 | 51.9 |

Figure 1. Installed capacity in 2030 by scenario.

Figure 2. Gas burnt for power in 2030 by scenario.

## 3.2 What one MWh saved avoids

| Scenario | vs | Cost (EUR/MWh) | CO2 (t/MWh) | Gas (MWh/MWh) | Capacity (MW per TWh) |
| --- | --- | --- | --- | --- | --- |
| S1-10 | S0 | 62.6 | 0.18 | 0.90 | 507 |
| S1-15 | S0 | 59.6 | 0.18 | 0.91 | 449 |
| S1-20 | S0 | 58.0 | 0.18 | 0.91 | 422 |
| S1-15C | S0 | 62.4 | 0.22 | 1.09 | 446 |
| S2-300 | S0 | 65.0 | 0.24 | 1.21 | 341 |
| S2-600 | S0 | 69.2 | 0.27 | 1.39 | 255 |
| G-lo-S1-15 | G-lo-S0 | 43.0 | 0.28 | 1.42 | 348 |
| G-hi-S1-15 | G-hi-S0 | 70.1 | 0.11 | 0.54 | 616 |

Figure 3. What each MWh saved avoids, against the reference at the same gas price.

## 3.3 Findings

Efficiency avoids new gas plant. The base case needs 423 MW of new gas turbines to keep the reserve margin. A 10% saving lowers the peak enough to avoid all of it, which is why the first 10% saved is worth the most (62.6 EUR/MWh against 59.6 for 15%). Beyond that point, further savings avoid mostly solar and wind that would otherwise be built.

Timing matters. In S1-15C only 39% of the 15% saving fits on the summer cooling load; the rest is an even cut. That is enough to avoid 20% more gas per MWh and 11.5 M EUR per year more than S1-15, because air-conditioning hours are the hours when gas runs.

Figure 4. The same 15% saved evenly or from cooling first.

Flexibility adds to efficiency. Shifting 300 MW of load saves 22.1 M EUR per year on top of S1-15, about 74,000 EUR per MW per year. The model moves morning and evening load into the midday solar hours, builds more solar and burns less gas. Under the reserve rule, flexibility gets no credit for lowering the peak, so all of this value is energy.

Figure 5. Dispatch in the week around the annual peak, S0 and S2-300.

The gas price changes the result most. With gas at x0.5, each MWh saved avoids 0.28 t of CO2, because the saving mostly displaces gas. With gas at x1.5, the reference system is already 70% renewable with 3,148 MWh of batteries, and each MWh saved avoids only 0.11 t of CO2 but 70 EUR.

Figure 6. Hourly electricity price, sorted, for S0, S1-15 and S2-300.

# 4. Limitations

Nothing limits how fast renewables are built. The base case adds 6.0 GW of solar and wind by 2030, far above Tunisia's recent pace. The results show what least cost would do, not a forecast.

The cost of efficiency programmes is not modelled. The avoided cost per MWh is the most a programme could cost and still pay off for the power system.

One weather year (2013) at 1-hour steps. A 3-hour test run built 2.7% more solar and 3.9% more wind.

Demand growth and the 2030 peak come from STEG's forecast as quoted by JICA (2022), a secondary source.

Imports are flat at their 2024 level, so every MWh saved falls on domestic generation.

The fitted efficiency factor for existing gas units also stands in for plant outages, which are not modelled.

The reserve margin is one national capacity rule, not a reliability study.

System cost includes the annualised cost of plants that already exist. Differences between scenarios are meaningful; the absolute level is not the cost of the real system.

# 5. Inputs and sources

Every input is a row of data/assumptions_register.xlsx with its unit, type and source; rows typed 'assumption' have no published source and are explained in the register notes. The study inputs:

| Input | Value | Unit | Type | Source |
| --- | --- | --- | --- | --- |
| re_target_2030 | 0.35 | share | sourced | TAP, 9 Oct 2026: Head of Government reaffirms 35% target |
| flex_cap_mw | 300 | MW | sourced | TAP, 9 Oct 2026: action plan targets 300 MW peak-demand reduction |
| flex_cap_hi_mw | 600 | MW | assumption |  |
| flex_max_hours | 3 | h | assumption |  |
| gas_price_factor_lo | 0.5 | x base | assumption |  |
| gas_price_factor_hi | 1.5 | x base | assumption |  |
| demand_growth | 0.032 | 1/yr | sourced | JICA / TEPSCO / KPMG, Data Collection Survey on Power Sector in Tunisia, Final Report (Mar 2022), quoting STEG's base-case forecast, p.2-17 and p.5-34 |
| peak_ref_2030_mw | 6,000 | MW | sourced | JICA / TEPSCO / KPMG, Data Collection Survey on Power Sector in Tunisia, Final Report (Mar 2022), quoting STEG's base-case forecast, p.2-17 and p.5-35 |
| discount_rate | 0.071 | 1/yr | sourced | PyPSA-Earth v0.10.0 config.default.yaml, costs.discountrate |
| demand_2024_twh | 22.51 | TWh | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025), table 'ELECTRICITE', printed p.18 |
| imports_2024_twh | 3.113 | TWh | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025), table 'ELECTRICITE', printed p.18 |
| gas_price_eur_per_mwh_th | 28.42 | EUR/MWh_th | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (gas, fuel); original: World Bank Commodity Markets 2025 and ENTSO-E/ENTSOG TYNDP 2024 |
| cap_2024_ccgt_mw | 2,527 | MW | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) |
| cap_2024_ocgt_mw | 2,457 | MW | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) |
| cap_2024_steam_mw | 660 | MW | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) |
| cap_2024_re_mw | 368 | MW | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) |
| cap_2024_total_mw | 6,012 | MW | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) |
| gen_2024_gas_twh | 18.16 | TWh | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) |
| gen_2024_oil_twh | 0.0719 | TWh | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) |
| gen_2024_hydro_twh | 0.016 | TWh | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) |
| gen_2024_wind_twh | 0.337 | TWh | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) |
| gen_2024_solar_twh | 0.6278 | TWh | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) |
| gen_2024_total_twh | 19.21 | TWh | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) |
| gas_share_2024 | 0.945 | share | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) |
| peak_2024_mw | 4,888 | MW | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) |
| steg_specific_consumption_2024 | 194.8 | toe(GCV)/GWh | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) |
| steg_demand_2030_gwh | 28,362 | GWh | sourced | JICA / TEPSCO / KPMG, Data Collection Survey on Power Sector in Tunisia, Final Report (Mar 2022), quoting STEG's base-case forecast, p.2-17 |
| load_factor_2030 | 0.54 | share | sourced | JICA / TEPSCO / KPMG, Data Collection Survey on Power Sector in Tunisia, Final Report (Mar 2022), quoting STEG's base-case forecast, p.5-34 |
| min_to_peak_2030 | 0.34 | share | sourced | JICA / TEPSCO / KPMG, Data Collection Survey on Power Sector in Tunisia, Final Report (Mar 2022), quoting STEG's base-case forecast, p.5-35 |
| ccgt_efficiency | 0.58 | per unit | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (CCGT, efficiency); original: Danish Energy Agency, inputs/technology_data_for_el_and_dh.xlsx |
| ccgt_vom | 5.61 | EUR/MWh | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (CCGT, VOM); original: Danish Energy Agency, inputs/technology_data_for_el_and_dh.xlsx |
| ocgt_efficiency | 0.41 | per unit | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (OCGT, efficiency); original: Danish Energy Agency, inputs/technology_data_for_el_and_dh.xlsx |
| ocgt_vom | 6.011 | EUR/MWh | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (OCGT, VOM); original: Danish Energy Agency, inputs/technology_data_for_el_and_dh.xlsx |
| gas_ncv_per_gcv | 0.9 | ratio | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024, conversion table (PDF p.22) |
| existing_gas_efficiency_factor | 0.8634 | x tech-data | assumption | Calibrated (Task 10) so the dispatch-only 2024 run matches STEG's measured fuel use: ONEM Memento 2024, specific consumption 194.8 toe(PCS)/GWh, PCI = 0.9 PCS |
| ocgt_investment | 581.4 | EUR/kW | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (OCGT, investment); original: Danish Energy Agency, inputs/technology_data_for_el_and_dh.xlsx |
| ocgt_fom | 1.78 | %/year | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (OCGT, FOM); original: Danish Energy Agency, inputs/technology_data_for_el_and_dh.xlsx |
| ocgt_lifetime | 25 | years | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (OCGT, lifetime); original: Danish Energy Agency, inputs/technology_data_for_el_and_dh.xlsx |
| gas_co2_intensity | 0.198 | tCO2/MWh_th | sourced | PyPSA technology-data v0.15.0 costs_2030.csv (gas, CO2 intensity); original: Stoichiometric calculation with 50 GJ/t CH4 |
| gas_for_power_2024_ktep_ncv | 3,168 | ktep (net CV) | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) |
| cap_2024_selfgen_solar_lv_mw | 315 | MW | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) |
| cap_2024_selfgen_solar_mvhv_mw | 125 | MW | sourced | ONEM / Ministry of Industry, Mines and Energy, Memento du secteur de l'énergie, Chiffres de 2024 (Aug 2025) |
| reserve_margin | 0.1 | share of peak | sourced | JICA / TEPSCO / KPMG, Data Collection Survey on Power Sector in Tunisia, Final Report (Mar 2022), p.5-33 |

# 6. Reproducing the study

The code, tests, scenario files and step-by-step instructions are in the repository README. One command (snakemake -j 1) rebuilds, solves and checks all 11 scenarios in about an hour on a laptop, and scripts/make_figures.py and scripts/make_report.py redraw the figures and this report.